## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: NHIDCL
Name of Work: Supplying, Installation & Commissioning of Fire Fighting System from Automated Car Parking Building in Transport Bhawan to Pump Room of Shram Shakti Bhawan, New Delhi.
Contract No: NHIDCL/ACP/Fire Fighting System/2018
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | BASIC RATE In Figures To be entered by the Bidder in Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT Without Taxes in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | Electrical Operated Terrace pump | BI01010001010000000000000515BI0100001112 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
1.01 | Supply, Installation, testing and commissioning of Electrical Motor(KILOSKAR MAKE) Driven Automatic pressurization (Terrace) pumping set consisting of the following as per specifications. a)Horizontally mounted centrifugal end suction type single stage fire pump (KILOSKAR MAKE) for building pressure loss due to any leakage in the system and capable to deliver approx. 900 lpm against a total head of 35 m having cast iron body, bronze impeller, stainless steel shaft . b) Squirrel cage induction motor totally enclosed fan cooled type suitable for 415 Volts + 15% 3 phase 50 HZ A.C supply of suitable capacity for the above pump with synchronous speed of 2900 RPM conforming to IS: 325 and duty coupled with above pump coupled with flexible coupling including earthing as per relevant Indian Standard and specifications. c) Common base frame/bed plate for mounting Pump and Motor fabricated of suitable M.S Channel as per manufacture’s recommendations. d) Suitable RCC pump foundations as per manufactures design and 4 Nos. Dunlop Anti vibration (cushy foot) heavy duty mounting pads. e) Suitable mechanical seal & 1 No. pressure gauge on the pump delivery line with gunmetal isolation cock. f) Coupling and coupling guard for direct coupling of motor and pump. | BI01010001010000000000000515BI0100001113 | 1 | Nos | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.02 | Dismentalling and replacing of existing Diesel pump set (2850LPM,70M Head ) from the pump Room | BI01010001010000000000000515BI0100001114 | 1 | Set | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.03 | SUPPLY ,INSTALLATION, TESTING &COMMISSIONING Diesel Engine Driven Fire Pumping set suitable for automatic operation consisting of the following as per specifications; a) Horizontally mounted, centrifugal type single stage / multi-stage fine fire pump having cast iron body ,bronze impeller,stainless steel shaft & capable of delivering 4500 lpm against a total head of 80 MTR, presser gauge with stop cock etc,on the delivery side including bypass arrangment( with 50 mm dia G.M.stop valve and upto 5M G.I .stop vave and upto 5M G.I Medium Pipes for periodical testing of the pumping set of the pumping set as per TAC rules. b) Water Cooled TAC Approved Diesel Engine Suitable for(1450/1800 RPM) for above pump complete with automatic starting mechanism ,batteries, automatic battery charger unit, flexible coupling with the pump, coupling with the pump, fuel tank, silencer, exhaust pipe & all standard accessories as required as per TAC rules including earthing, mandatory spares and tool kit. c) Common bed Plate for mounting pump and Engine Fabricated of suitable M.S Channel as per manufactureera recommendations. d) Suitable for RCC pump foundation as per manufacturers desugn ,8 nos Dunlop anti vibration (cushy foot) heavy duty mounting pads. | BI01010001010000000000000515BI0100001115 | 1 | Set | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2 | Electrical Operated Sprinkler main Pump | BI01010001010000000000000515BI0100001116 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
2.01 | Supply, Installation, testing and commissioning of electrical driven Main Fire Pump suitable for automatic operation consisting of the following: complete in all respect as required. a) Horizontally type, single/multistage, centrifugal split casing pump of cast iron body, bronze impeller with stainless steel shaft, mechanical seal to ensure a minimum pressure of 3.5 Kg/ cm2 at highest and farthest outlet at a specified flow of 2850 lpm at 60 m head conforming to IS 1520 .KILOSKAR MAKE. b) Suitable HP squirrel cage induction motor, totally enclosed fan cooled type, synchronous speed 1500 RPM, suitable for operation on 415 Volts, 3 phase, 50HZ, A.C. supply with IP 55 class of protection for enclosure, horizontal foot mounted type with class- 'F' insulation, conforming to IS:325. c) MS fabricated common base plate, coupling, coupling guard, foundation bolts etc. as required. d) Suitable cement concrete foundation as per manufacturers design duly plastered with 4 nos. Dunlop (cushy foot) heavy duty Anti vibration mounting pads. | BI01010001010000000000000515BI0100001117 | 1 | Set | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
3 | Jockey Pump for Sprinkler | BI01010001010000000000000515BI0100001118 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
3.01 | Supply, Installation, testing and commissioning of electrical driven pressurisation pump suitable for automatic operation consisting of the following: complete in all respect as required. a) Horizontally type, single/multistage, centrifugal pump of cast iron body, bronze impeller with stainless steel shaft, mechanical seal and flow of 180 LPM at 60 m head conforming to IS 1520. KILOSKAR MAKE b) Suitable HP squirrel cage induction motor, totally enclosed fan cooled type, suitable for operation on 415 Volts, 3 phase, 50HZ, A.C. supply with IP 55 class of protection for enclosure, horizontal foot mounted type with class- 'F' insulation, conforming to IS:325 c) MS fabricated common base plate, coupling, coupling guard, foundation bolts etc. as required. d) Suitable cement concrete foundation as per manufacturers design duly plastered with 4 nos. Dunlop (cushy foot) heavy duty Anti vibration mounting pads. | BI01010001010000000000000515BI0100001119 | 1 | Set | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
3.02 | Supply installation, testing and commissioning of 100 Lpd SWHS ETC Type ARINNA make SWH System Consists -Tank –SS 304 in 1 mm thick and 50 mm thick puff insulation covered with GI powder coated cladding sheet, Tank Stand, 10 tube Collector dia 58mm and length 1800mm, 1.5 kw Electric Heating Elements with thermostat controlling ,along with suitable foundation for solar system on terrace level. | BI01010001010000000000000515BI0100001120 | 1 | Set | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
3.03 | Dismantling and shifting of Exiting M.S.Pipe line IN EXISTING PUMP ROOM of S.S.B.B for required new installation of Pump suction and header pipe along with Fire Fighting Electrical panel IN EXISTING PUMP ROOM ,and all as per requirement | BI01010001010000000000000515BI0100001121 | 1 | Lot | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
4 | Pump Room Piping ,Supply, Installation, Testing & Commissioning of heavy class Mild Steel pipe confirming to (IS:1239 Part -I up to 150mm dia and IS 3589 above 200mm dia of Class 2, with minimum 6.00mm thickness) including cutting, threading, welding, jointing with all fittings i.e tees, bends, elbows reducers, clamps, hangers etc. including cutting holes in brick or RCC walls/ slabs and making good the same complete including painting with one coat of primer and two or more coats of synthetic enamel paint of approved make and shade including all MS structural steel work for supporting and hanging the pipes. (for all suction and delivery header pipes and exposed pipes in the plant room) Note: Pipes upto and 50 mm dia shall be threaded joints and above 50mm shall be welded joints.along with suitable foundation for pipe laying on groun level | BI01010001010000000000000515BI0100001122 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
4.01 | 250 mm dia (as per IS 3589, class c, minimum 6.0 mm thick) | BI01010001010000000000000515BI0100001123 | 15 | Meter | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
4.02 | 150 mm dia (as per IS 1239, class c, minimum 6.0 mm thick) for the Building out side area up to pump room | BI01010001010000000000000515BI0100001124 | 180 | Meter | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
4.03 | 100 mm dia (as per IS 1239, class c, minimum 4.0 mm thick) for building | BI01010001010000000000000515BI0100001125 | 20 | Meter | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
4.04 | 40 mm dia (as per IS 1239, class c, minimum 4.0 mm thick) for building | BI01010001010000000000000515BI0100001126 | 30 | Meter | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
5 | Providing, fixing, testing and commissioning of pressure switch. | BI01010001010000000000000515BI0100001127 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
5.01 | Providing, fixing, testing and commissioning of pressure switch 0-10 bar range | BI01010001010000000000000515BI0100001128 | 18 | Each | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
6 | Supply Installation,testing and commissioning of Pressure Release Valve. | BI01010001010000000000000515BI0100001129 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
6.01 | Supply Installation,testing and commissioning of Pressure Release Valve of gunmetal and 25 mm dia with gunmatel valve for sprinkler and hydrant system | BI01010001010000000000000515BI0100001130 | 5 | Each | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
7 | Providing, fixing, testing and commissioning of butterfly valve of rating PN 1.6 with bronze/ gunmetal seat duly ISI marked complete with nuts, bolts, washers, gaskets, conforming to I.S:13095 of following sizes as required. | BI01010001010000000000000515BI0100001131 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
7.01 | 250 mm dia | BI01010001010000000000000515BI0100001132 | 3 | Each | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
7.02 | 200 mm dia | BI01010001010000000000000515BI0100001133 | 3 | Each | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
7.03 | 150 mm dia | BI01010001010000000000000515BI0100001134 | 3 | Each | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
7.04 | 100 mm dia | BI01010001010000000000000515BI0100001135 | 2 | Each | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
7.05 | 80 mm dia | BI01010001010000000000000515BI0100001136 | 6 | Each | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
8 | Providing, fixing, testing and commissioning of dual plate non return valve of following sizes conforming to I.S: 5312 of rating PN 1.6 complete with rubber gaskets, nuts, GI bolts, washers, etc.as required. | BI01010001010000000000000515BI0100001137 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
8.01 | 250 mm dia | BI01010001010000000000000515BI0100001138 | 1 | Each | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
8.02 | 150 mm dia | BI01010001010000000000000515BI0100001139 | 2 | Each | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
8.03 | 100 mm dia | BI01010001010000000000000515BI0100001140 | 1 | Each | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
8.04 | 80 mm dia | BI01010001010000000000000515BI0100001141 | 3 | Each | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
8.05 | 65 mm dia | BI01010001010000000000000515BI0100001142 | 3 | Each | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
9 | Providing and fixing of suitable flexible neoprene rubber expansion joint, single arch with integral rubber flanges tested at 20 Kg/cm2 with SRR drilled as per BS-10, Table-D, complete. | BI01010001010000000000000515BI0100001143 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
9.01 | 200 mm dia | BI01010001010000000000000515BI0100001144 | 1 | Each | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
9.02 | 150 mm dia | BI01010001010000000000000515BI0100001145 | 3 | Each | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
9.03 | 100 mm dia | BI01010001010000000000000515BI0100001146 | 1 | Each | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
9.04 | 80 mm dia | BI01010001010000000000000515BI0100001147 | 3 | Each | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
9.05 | 65 mm dia | BI01010001010000000000000515BI0100001148 | 3 | Each | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
10 | Providing and making of 200 mm machine core cutting. | BI01010001010000000000000515BI0100001149 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
10.01 | Providing and making of 200 mm machine core cutting for crossing of sprinkler pipe in S.S.B.B pump room as per the instruction: | BI01010001010000000000000515BI0100001150 | 1 | Nos | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
11 | Supply , Installation ,testing and Commissioning FOR CAR ELEVATOR PIT OF DRAINAGE sump PUMP. | BI01010001010000000000000515BI0100001151 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
11.01 | Supply , Installation ,testing and Commissioning FOR CAR ELEVATOR PIT OF DRAINAGE sump PUMP (modle no-AP12-50-11-A1) , with float control system of grundfos make 10 to 15 meter head ,stenles steel body along with al wiring and conduiting & as per the requirement of the site conditions . | BI01010001010000000000000515BI0100001152 | 3 | Nos | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
12 | FIRE FIGHTING ELECTRICAL WORK | BI01010001010000000000000515BI0100001153 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
12.01 | Providing and fixing combined electrical starter panel for the terrace pump ,1 Set - (1 No. Terrace fire Pump) Fully Automatic Star delta Starter up to 15 HP complete with Contactors with 2NO + 2NC for remote operations, Start/ Stop Push Buttons, Single Phase Preventor Relay (Current Base), ON/ OFF Indication lamps & Ammeter with CT's of suitable ratings. | BI01010001010000000000000515BI0100001154 | 1 | Nos | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
12.02 | Design, Supply, installation, testing & commissioning of main fire pump panel cubical type CRCA sheet steel free standing indoor type motor control centre with Aluminium bus bars, LED type indicating lamps, dust & vermin proof doors, interlock, interconnection with under noted mountings as per specifications (Main Fire Pump Panel). INCOMER:- i) 1 No. - 400 Amps. TPN MCCB ( 36 KA ) ii) 1 Set -(0-400A) Ammeter with selector switch & CT's iii) 1 Set -(0-500V) Voltmeter with selector switch & control fuses. iv) 1 Set -Phase indication lights ( R, Y, B ). v) BUS BARS:-500Amps. TP&N aluminium bus bars (35 KA). OUT GOINGS:- i) 3 Nos.-200/140 AMP, TP+NL, MCCB (35 KA). ii) 4,Nos.-100/32 AMP, TP, MCCB (35 KA). iiii) 6Nos.- 6 to 32Amp., SP & 4Nos.- 32Amp.,TPN, MCB's (10 KA) Controlled by 1No. 32Amp.4 Pole MCB (10 KA). iv) 1 Set -(1 Nos. Main Hydrant Pump) Fully Automatic Star delta Starter up to 75 HP complete with Contactors with 2-NO + 2NC for remote operations, Start/ Stop Push Buttons, Single Phase Preventor Relay (Current Base), ON/ OFF Indication lamps & Ammeter with CT's of suitable ratings. v) 1 Set -(1 Nos. Main Sprinkler Pump) Fully Automatic Star delta Starter up to 75 HP complete with Contactors with 2-NO + 2NC for remote operations, Start/ Stop Push Buttons, Single Phase Preventor Relay (Current Base), ON/ OFF Indication lamps & Ammeter with CT's of suitable ratings., vi) 1 Set - (1 No. Jockey Pump for Hydrant) Fully Automatic Star delta Starter up to 20.0 HP complete with Contactors with 2NO + 2NC for remote operations, Start/ Stop Push Buttons, Single Phase Preventor Relay (Current Base), ON/ OFF Indication lamps & Ammeter with CT's of suitable ratings. vii) 1 Set - (1 No. Jockey for Sprinkler system) Fully Automatic Star delta Starter up to 20.0 HP complete with Contactors with 2NO + 2NC for remote operations, Start/ Stop Push Buttons, Single Phase Preventor Relay (Current Base), ON/ OFF Indication lamps & Ammeter with CT's of suitable ratings. viii) 1 Set - (1 No. Diesel Pump) Fully Automatic engine starting system complete with battery charger hooter, indicating lights transformer, rectifier, timer voltmeter, ammeter, selector, switches, push buttons auxiliary relay etc. complete as required. | BI01010001010000000000000515BI0100001155 | 1 | Set | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
12.03 | Supplying, laying, connecting, testing & commisioning of under noted size of PVC insulated, PVC sheathed armoured and overall PVC sleaved control cables 2C x 1.5 sq.mm copper solid cunductor | BI01010001010000000000000515BI0100001156 | 50 | Meter | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
13 | Supplying, laying, connecting, testing & commissioning of under noted sizes of aluminium / copper conductor XLPE insulated, PVC sheathed armoured and overall PVC sleeved 1.1 KV grade power distribution cables in pipe, wall, racks, cable trays, including, dressing, clamping with M.S Zinc passivated clamps etc as required conforming to relevant IS code and technical specifications. | BI01010001010000000000000515BI0100001157 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
13.01 | 3.5C x 95 sq.mm (Aluminium) | BI01010001010000000000000515BI0100001158 | 70 | Meter | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
13.02 | 3.5C x 50 sq.mm (Aluminium) | BI01010001010000000000000515BI0100001159 | 70 | Meter | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
13.03 | 3.5C x 35 sq.mm (Aluminium) | BI01010001010000000000000515BI0100001160 | 70 | Meter | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
13.04 | 3.5C x 25 sq.mm (Aluminium) | BI01010001010000000000000515BI0100001161 | 75 | Meter | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
13.05 | 4C x 16 sq.mm (Aluminium) | BI01010001010000000000000515BI0100001162 | 80 | Meter | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
13.06 | D.G Control cable, 8 core 2.5 sqmm Single stand copper cable. | BI01010001010000000000000515BI0100001163 | 65 | Meter | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
14 | Supply and making end termination with brass single compression gland including providing and crimping of aluminium/copper solder less lugs/ferrules for XLPE/ PVC armoured/ Unarmoured aluminium/ copper conductor cable 1.1 KV grade of following sizes: | BI01010001010000000000000515BI0100001164 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
14.01 | 3.5C x 95 sq.mm (Aluminium) | BI01010001010000000000000515BI0100001165 | 14 | Nos | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
14.02 | 3.5C x 50 sq.mm (Aluminium) | BI01010001010000000000000515BI0100001166 | 12 | Nos | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
14.03 | 3.5C x 35 sq.mm (Aluminium) | BI01010001010000000000000515BI0100001167 | 12 | Nos | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
14.04 | 3.5C x 25 sq.mm (Aluminium) | BI01010001010000000000000515BI0100001168 | 8 | Nos | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
14.05 | 4C x 16 sq.mm (Aluminium) | BI01010001010000000000000515BI0100001169 | 8 | Nos | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
15 | Supply and fixing of home UPS | BI01010001010000000000000515BI0100001170 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
15.01 | Supply and fixing of home UPS of rating 3.6 KVA (Single Phase) with 30 mins power back-up, 1 Nos ups DB double door with 32 amp D.P MCB,incomer and 6 , Nos 6 Amp S.P MCB for out going supply along with all accessories and as per requirement.and along with Redium Emergency Exit Signage ( size- 350X200) 25 nos | BI01010001010000000000000515BI0100001171 | 1 | Nos | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
16 | 150 mm dia. Installation Control Valve assembly. | BI01010001010000000000000515BI0100001172 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
16.01 | 150 mm dia. Installation Control Valve assembly comprising of vertical wet alarm valve, including 150 mm dia butterfly valve, hydraulic alarm motor & gong, 15 mm dia. Test valve, 50 mm dia. Drain valve and all necessary trimming connections including 2 nos.pressure guages as per manufacturer 's catalogue (UL/FM/LPC/TAC listed/approved). | BI01010001010000000000000515BI0100001173 | 1 | Nos | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
17 | Air Vessel for Fire Pump | BI01010001010000000000000515BI0100001174 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
17.01 | Air Vessel for Fire Pump Providing and fixing flanged end vertical air vessel fabricated from 8mm M.S. plate with dished ends from 10mm M.S. plate, one standard pressure tight manhole, painted inside with bitumasitc or anit-corrosive paint and outside with one coat of primer and two coats of syntheitc enamel paint of approved shade, complete with approved quality of pressure switches, pressure gauge, air release valve with shut off valve and having MS legs grouted in cement concrete, complete with all other required accessories to operate commonly main fire pump & Jockey pump at drop of pressure, automatically at required pressure setting. (To be tested at 25kg/cm2 and to be placed in the Fire Pump room) Recommended dia : 450mm, Height of shell : 2000mm | BI01010001010000000000000515BI0100001175 | 1 | Set | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
Total in Figures | [51 empty] | #VALUE! | #VALUE! | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information